GF Building Flow Solutions

6510 Kennedy Road

Mississauga, ON L5T 2X4

888 994 7726

www.uponor.com

## SECTION 23 83 16

### RADIANT HEATING AND COOLING EQUIPMENT

- GENERAL

  - SECTION INCLUDES

    - Hydronic radiant heating and cooling distribution system.

      - Provide labor, materials, transportation, equipment and services to install a hydronic radiant and cooling system where indicated on the Contract Drawing and specified herein.

      - Provide labor, materials, transportation, equipment and services to install a PEX hydronic distribution system where indicated on the Contract Drawing and specified herein.

  - RELATED SECTIONS

      - Section 23 21 13 – Hydronic Piping

      - Section 23 21 13.13 – Underground Hydronic Piping

  - REFERENCES

    - General: Standards listed by reference, including revisions by issuing authority, form part of this specification section to extent indicated. Standards listed are identified by issuing authority, authority abbreviation, designation number, title, or other designation established by issuing authority. Standards subsequently referenced herein are referred to by issuing authority abbreviation and standard designation.

    - American Society for Testing and Materials (ASTM):

      - ASTM F876 Standard Specification for Cross-Linked Polyethylene (PEX) Tubing.

      - ASTM F877 Standard Specification for Cross-Linked Polyethylene (PEX) Plastic Hot and Cold Water Distribution Systems.

      - ASTM F2788 Standard Specification for Metric-Sized PEX Pipe.

      - ASTM F1960 Standard Specification for Cold Expansion Fittings with PEX Reinforcing Rings for Use with Cross-Linked Polyethylene (PEX) Tubing.

    - National Sanitation Foundation (NSF):

      - NSF/ANSI 14 Plastic Piping System Components and Related Materials.

      - NSF/ANSI 61 Drinking Water System Components – Health Effects.

    - Underwriters’ Laboratories of Canada Inc:

      - CAN/ULC-S101 Standard Methods of Fire Endurance Tests of Building Construction and Materials.

      - CAN/ULC-S115 Standard Method of Fire Tests of Firestop Systems.

      - CAN/ULC-S102.2 Standard for Surface Burning Characteristics of Flooring, Floor Covering and Miscellaneous Materials and Assemblies.

    - Canadian Standards Association (CSA):

      - CAN/CSA B137.5 Cross-Linked Polyethylene (PEX) for Pressure Applications.

      - CAN/CSA B214 Installation Code for Hydronic Heating Systems.

    - German Institute of Standards (DIN):

      - DIN 4726 Warm Water Floor Heating Systems and Radiator Connections – Piping Made Out of Plastic Materials.

    - Plastics Pipe Institute (PPI):

      - PPI Technical Report TR-4.

    - Uponor Ltd.

      - Uponor Complete Design Assistance Manual (CDAM), current edition.

      - Uponor LoopCAD® Software.

      - Uponor Residential Radiant and Hydronics Installation Handbook, current edition.

      - Uponor PEX Piping Systems Design and Installation Manual (PDIM), current edition.

  - SYSTEM DESCRIPTION

    - Performance Requirements: Provide hydronic radiant heating and cooling system which has been manufactured, fabricated and installed to comply with regulatory agencies and to maintain performance criteria stated by manufacturer without defects, damage or failure. The floor loop design shall be capable of providing the specified heating and cooling loads without altering the flow output of the specified circulators.

    - Performance Requirements: Provide PEX tubing hydronic distribution system which has been manufactured, fabricated and installed to comply with Federal, Provincial and Municipal plumbing and building codes and to maintain performance criteria stated by manufacturer without defects, damage or failure.

  - SUBMITTALS

    - General: Submit listed submittals in accordance with Conditions of the Contract and Division 1 Submittal Procedures Section.

    - Product Data: Submit product data for specified products.

      - Submit verification of Standard Grade hydrostatic pressure ratings from Plastic Pipe Institute in accordance with TR-4. The following 3 Standard Grade ratings are required:

        - 200°F (93°C) at 80 psi (551 kPa).

        - 180°F (82°C) at 100 psi (689 kPa).

        - 73°F (23°C) at 160 psi (1102 kPa).

      - Submit Product Submittal sheets for tubing, pre-insulated tubing, manifolds, brackets, supports, connection system, valves, fittings, loop and/or manifold actuators, thermostats, and zone controls.

    - Performance Data: Submit proof of qualification and experience by manufacturer who designed the project. Submit manufacturer’s design calculations showing compliance with meeting heat and cooling loads based on maximum [specify]°F ([specify]°C) average heating supply water and maximum [specify]°F ([specify]°C) entering cooling supply water. Additional design calculations shall include:

      - Flowrate in each loop

      - Head loss in each loop

      - Surface temperature(s)

      - Loop design temperature drop(s)

      - Loop spacing(s)

      - Loop length(s)

    - Regulatory Listings: Submit applicable UL, ULC, Warnock Hersey, Intertek or QAI and CSA or NSF listings as proof of compliance with Federal, Provincial and Municipal building codes. Listings shall include the following.

      - Submit listings that indicate that the PEX tubing system has been listed to CAN/ULC-S101 when the PEX tubing is incorporated in and traverses a CAN/ULC-S101 rated assembly. The listings must be appropriate to assemblies on site.

      - Submit listings that indicate that the PEX tubing firestop system has been listed to CAN/ULC-S115 when the PEX tubing penetrates a fire separation. The listings must be appropriate to assemblies on site.

      - Submit listings that indicate that the PEX tubing has been listed to CAN/ULC-S102.2 for maximum 25 flame spread and maximum 50 smoke developed.

    - Shop Drawings: Submit design print-out of Uponor LoopCAD and shop drawings indicating loop layout, manifold locations, initial loop flow balance settings, floor profiles, floor coverings and product components, including anchorage, accessories and finishes.

      - Include installation drawings of tubing layout indicating loop length, loop spacing, tube size and detail notes to aid in installation of system.

      - No fabrication shall be performed until approval is given.

    - Quality Assurance Submittals: Submit the following:

      - Copy of certificate indicating that the installer is certified in the installation of the manufacturer’s products.

      - Manufacturer’s Instructions: Manufacturer’s installation instructions.

      - Installer shall provide in writing to the project owner that the PEX tubing and components furnished under this specification conforms to the material and mechanical requirements specified herein.

      - Installer shall provide manufacturer’s letter that any firestop coming in contact with the PEX tubing is chemically compatible with the PEX tubing.

      - Submit CSA listing that the PEX tubing, PEX rings and PEX fittings from the same manufacturer have been tested together and certified as a system.

    - Closeout Submittals: Submit the following:

      - Operation and Maintenance Data: Operation and maintenance data for installed products in accordance with Division 1 Closeout Submittals (Maintenance Data and Operation Data) Section including methods for maintaining installed products and precautions against cleaning materials and methods detrimental to finishes and performance.

      - Warranty: Warranty documents specified herein.

      - Manufacturer’s Field Reports: Manufacturer’s field reports specified herein.

      - Final “As-Built” loop layout drawing.

      - Copy of Uponor LoopCAD software printout.

      - Record Documents: Project record documents for installed materials in accordance with Division 1 Closeout Submittals (Project Record Documents) Section.

  - QUALITY ASSURANCE

    - Qualifications:

      - Installer Qualifications: Installer shall be experienced in performing work of this section and has specialized in installation of work similar to that required for this project.

      - Installation Qualifications: Installation must be by skilled tradesmen holding a trade qualification license or apprentices under the supervision of a licensed tradesman.

      - Installer Qualifications: Installer must be recognized by the manufacturer as a “Trained Installer”.

    - Regulatory Requirements: PEX tubing and components shall be installed in full compliance with all Federal, Provincial and Municipal codes, standards and requirements. In particular:

      - PEX tubing shall be listed to a maximum 25 flame spread and maximum of 50 smoke developed per the requirements of CAN/ULC-S102.2.

        - As outlined in CAN/ULC S102 Appendix Section A1.23, Plastic Fittings and Valves, fittings shall be tested and listed by being mounted to plastic pipe in a method that is representative of field installation.

        - Up to 2 inch PEX tubing, plastic fittings and PEX rings shall be listed to a maximum 25 flame spread / 50 smoke developed with no spacing requirements or,

        - Up to 3 inch PEX tubing, plastic fittings and PEX rings shall be listed to a maximum 25 flame spread / 50 smoke developed with the rated insulations.

      - PEX tubing penetrating a fire separation shall be sealed per CAN/ULC-S115.

      - PEX tubing contained within a CAN/ULC-S101 floor/ceiling assembly shall be listed per CAN/ULC-S101.

    - Pre-installation Meetings: Conduct pre-installation meeting to verify project requirements, substrate conditions, floor coverings, manufacturer’s installation instructions and manufacturer’s warranty requirements. Comply with Division 1 Project Management and Coordination (Project Meetings) Section.

  - DELIVERY, STORAGE, AND HANDLING

    - General: Comply with Division 1 Product Requirements Sections.

    - Ordering: Comply with manufacturers’ ordering instructions and lead-time requirements to avoid construction delays.

    - Delivery: Deliver materials to job site in manufacturer’s original, unopened, undamaged containers with identification labels intact.

    - Storage and Protection: Store materials protected from exposure to harmful weather and job site conditions.

      - Store PEX tubing in original packaging or under cover to avoid dirt or foreign material from being introduced into the tubing.

      - Do not expose PEX tubing to direct sunlight for more than 30 days. If construction delays are encountered, installer is responsible for providing cover to portions of tubing exposed to direct sunlight.

  - WARRANTY

    - Project Warranty: Refer to Conditions of the Contract for project warranty provisions.

    - PEX Manufacturer’s Warranty: Warranty must meet the following conditions:

      - Wirsbo hePEX™ tubing shall carry a 30-year non-prorated warranty against failure due to defect in material or workmanship.

      - Uponor helioPEX™ X2 tubing shall carry a 25-year non-prorated warranty against failure due to defect in material or workmanship.

      - Manifolds and compression fittings shall carry a 5-year non-prorated warranty against failure due to defect in material or workmanship.

      - ProPEX® Fittings shall carry a twenty-five (25) year non-prorated warranty against failure due to defect in material or workmanship.

      - All tubing manufacturer’s valves and stops shall carry a one (1) year non-prorated warranty against failure due to defect in material or workmanship, except for commercial ball valves that shall carry a five (5) year non-prorated warranty.

      - Controls and electrical components shall carry a 2-year non-prorated warranty against failure due to defect in material or workmanship.

      - The ProPEX assembly of manufacturer’s tubing and fittings shall carry a twenty-five (25) year non-prorated warranty on maintaining a leak-proof seal.

      - Warranty shall provide for repair or replacement of any tube or fittings which are proven to be defective and pay for consequential damages.

      - Warranty shall be transferable to subsequent owners.

      - Effective Warranty: Current manufacturer’s warranty at time of installation.

      - Warranty Period: Warranty shall commence on date the products are installed.

  - SYSTEM STARTUP AND OWNER’S INSTRUCTION

    - System Startup: [Specify system startup requirements].

    - Owner’s Instruction: Instruct Owner’s personnel in operation and maintenance of installed units. Provide manufacturer’s installation, operation, and maintenance instructions for installed units.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable manufacturer: GF Building Flow Solutions (Uponor Ltd.), located at: 
6510 Kennedy Road; Mississauga, ON, L5T 2X4; tel: 888 994 7726
email: NAspecifications@uponor.com; web: www.uponor.com

      - Proprietary System: Wirsbo hePEX™ Radiant Heating and Cooling System.

      - Proprietary System: Uponor helioPEX™ X2 Radiant Heating and Cooling System.

  - PRODUCT SUBSTITUTIONS

    - Substitutions: No substitutions permitted.

    - Requests for substitutions will be considered in accordance with provisions of Section 01 60 00 — Product Requirements.

  - RADIANT HEATING AND COOLING PIPING AND FITTINGS

    - Performance requirements:

      - Oxygen Barrier: Tube shall have an oxygen barrier capable of limiting oxygen migration through the tube wall to no greater than 0.10 g/m3/day at 104°F (40°C) water temperature per the requirements of DIN 4726.

      - PEX tubing shall be CSA B137.5 listed for both hydronic and potable water distribution systems.

      - PEX tubing shall be manufactured in accordance with ASTM F876 and ASTM F877. The tube shall be listed to ASTM by an independent third party agency.

      - PEX tubing shall be ASTM F876 tested and approved for excessive temperature and pressure for 725 hours at 210°F (99°C) at 150 psi (1035 kPa).

      - Temperature and pressure ratings shall be issued by the Plastics Pipe Institute (PPI), a division of the Society of the Plastic Industry (SPI), tubing shall have Standard Grade hydrostatic design and pressure ratings of:

        - 200°F (82°C) at 80 psi (551 kPa).

        - 180°F (82°C) at 100 psi (689 kPA).

        - 73°F (23°C) at 160 psi (1102 kPa).

      - Minimum bend radius for cold bending of the PEX tubing shall not be less than 6 times the outside diameter. Bends with a radius less than stated shall require the use of a bend support as supplied by tube manufacturer.

      - PEX tubing dimensions shall be: [specify dimensions below]

        - 1/2 inch (15 mm) nominal inside diameter in accordance with ASTM F876.

        - 5/8 inch (18 mm) nominal inside diameter in accordance with ASTM F876.

        - 3/4 inch (20 mm) nominal inside diameter in accordance with ASTM F876.

        - 1 inch (25 mm) nominal inside diameter in accordance with ASTM F876.

        - 1-1/4 inch (32 mm) nominal inside diameter in accordance with ASTM F876.

        - 1-1/2 inch (40 mm) nominal inside diameter in accordance with ASTM F876.

        - 2 inch (50 mm) nominal inside diameter in accordance with ASTM F876.

        - 2-1/2 inch (65 mm) nominal inside diameter in accordance with ASTM F876.

        - 3 inch (80 mm) nominal inside diameter in accordance with ASTM F876.

    - Piping:

      - Wirsbo hePEX

        - PEX-a (Engel-method crosslinked polyethylene) SDR 9, ASTM F876 and F877 (CAN/CSA-B137.5) with an oxygen barrier meeting DIN 4726. 1/2 inch (16 mm) through 3 inch (80 mm) nominal pipe size.

      - Uponor helioPEX X2

        - PEX-x (proprietary crosslinked polyethylene) SDR 9, ASTM F876 and F877 (CAN/CSA-B137.5) with an oxygen barrier meeting DIN 4726. 1/2 inch (16 mm) through 3/4 inch (19 mm) nominal pipe size.

    - Pre-Insulated Tubing: All 1/2 inch to 1-1/2 inch PEX tubing that is required to be insulated shall be pre-insulated with the appropriate thickness of foam insulation as per local Code or as per ASHRAE 90.1.

      - Pre-insulated tubing shall be supplied by the PEX tubing manufacturer.

***NOTE to specifier*** [Select one manifold type below in “.2” below]. Engineered Polymer (EP) manifold c/w visual loop flow meters, max.15.4 gpm for 8-loop manifold; 1” Stainless steel, c/w visual loop flow meters, max. 14 gpm for 12 –loop manifold; 1 1/4” Stainless steel, max. c/w visual loop flow meters, max. 21 gpm for 12 –loop manifold;

      - Manifold Materials: Engineered Polymer (EP) manifold shall be fully assembled and mounted on a durable bracket with air vents and drains on both the supply and return manifold sections. Manifold shall be designed to handle maximum 15.4 gpm on 8-loop manifold. Manifold shall have R32 unions on the inlet side of the manifold to allow for various connection adapters. Visual flow meters shall be pre-mounted on the manifold assembly. Manifold shall be capable of full flow isolation on each loop.

        - Manifold Type: Uponor Engineered Polymer (EP) Manifold.

        - Manifolds shall be supplied by the PEX tubing manufacturer.

        - Manifolds shall have integral manual air vents on supply and return

        - Manifolds shall be manufactured from Engineered Polymer (EP).

        - Manifolds shall be supplied with manufacturers mounting brackets.

        - Manifolds shall be pre-assembled with visual flow indicators.

      - Manifold Materials: 1 inch Stainless-Steel Manifold shall be fully assembled and mounted on a durable bracket with air vents and drains on both the supply and return manifold sections. Manifold shall be designed to handle maximum 14 gpm for 12-loop manifold. The included manifold supply and return ball valves come with an R32 x 1 inch NPT connection and thermometers. Visual flow meters shall be pre-mounted on the manifold assembly. Manifold shall be capable of full flow isolation on each loop

        - Manifold Type: Uponor 1 inch Stainless-Steel Manifold.

        - Manifolds shall be supplied by the PEX tubing manufacturer.

        - Manifolds shall have integral manual air vent and drain on the supply and return manifold.

        - Manifolds shall be manufactured from Stainless steel

        - Manifolds shall be supplied with manufacturers mounting brackets.

        - Manifolds shall have 1 inch internal barrel diameter.

      - Manifold Materials: 1-1/4 inch Stainless-Steel Manifold shall be fully assembled and mounted on a durable bracket with air vents and drains on both the supply and return manifold sections. Manifold shall be designed to handle maximum 21 gpm for 12-loop manifold. The included manifold supply and return ball valves come with an R32 x 1 inch NPT connection for 2 to 7 loop models and R32 x 1-1/4 inch NPT connection for 8 to 12 loop models. Ball valves come equipped with thermometers. Visual flow meters shall be pre-mounted on the manifold assembly. Manifold shall be capable of full flow isolation on each loop

        - Manifold Type: Uponor 1-1/4 inch Stainless-Steel Manifold.

        - Manifolds shall be supplied by the PEX tubing manufacturer.

        - Manifolds shall have integral manual air vent and drain on the supply and return manifold.

        - Manifolds shall be manufactured from Stainless steel

        - Manifolds shall be supplied with manufacturers mounting brackets.

        - Manifolds shall have 1-1/4 inch internal barrel diameter

      - Manifold Materials: Commercial Stainless-Steel Manifold shall be fully assembled and mounted on a durable bracket with air vent and drain on the supply and return manifold sections. Manifold shall be designed to handle maximum 48 gpm for 12-loop manifold. The included manifold supply and return ball valves come with an G2 male x 1-1/2 inch FNPT connection for 3 to 12 loop models. Manifolds come equipped with thermometers. Visual flow meters shall be pre-mounted on the manifold assembly. Manifold shall be capable of full flow isolation on each loop

        - Manifold Type: Commercial Stainless-steel manifold assembly.

        - Manifolds shall be supplied by the PEX tubing manufacturer.

        - Manifolds shall have integral manual air vent and drain on the supply and return manifold.

        - Manifolds shall be manufactured from stainless steel.

        - Manifolds shall be supplied with manufacturers mounting brackets.

        - Manifolds shall have a 2 inch internal barrel diameter.

      - Manifold Isolation Ball Valves (for EP manifolds only): Manifolds shall be isolated at the inlet and outlet of the manifold with full-flow ball valves.

        - Isolation Ball Valve Type: Uponor supply and return ball valves.

        - Isolation ball valves shall be supplied by the PEX tubing manufacturer.

      - Manifold Fitting Materials: Fittings shall be manufactured of brass. Fittings shall be nose-cone insert-type compression fitting, nose-cone insert-type swivel fitting, or PEX-a cold expansion type fitting.

        - Fittings shall be supplied by the PEX tubing manufacturer.

        - Compression fitting shall be an assembly consisting of nose cone insert, compression ring and compression nut.

        - Swivel fitting shall be an assembly consisting of nose cone insert, swivel nut, and PEX-a cold expansion ring.

        - PEX-a cold expansion type fitting shall be an assembly consisting of insert and PEX-a cold expansion ring.

      - ProPEX fitting Materials: Fittings shall be manufactured of Engineered Polymer (EP). Lead free brass materials are allowed only for transition fittings. Fitting connections shall be made to the requirements of ASTM F1960.

        - Fittings shall be supplied by the PEX tubing manufacturer.

        - PEX-a cold expansion type fittings shall be an assembly consisting of insert and PEX-a cold expansion ring.

        - Polymer Fitting Type: Uponor Engineered Polymer (EP) fittings.

        - Brass Fitting Type: Uponor lead free brass fittings.

      - Supply and Return Piping to Manifolds: Piping run in heated spaces shall be cross-linked tubing with oxygen diffusion barrier capable of limiting oxygen migration through the tube wall to no greater than 0.10 g/m3/day at 104°F (40°C) water temperature per the requirements of DIN 4726. Supply and return piping run underground shall be crosslinked tube encased in a pre-insulated polyethylene corrugated jacket.

        - Supply and Return Piping Type: Wirsbo hePEX tubing.

        - Supply and Return Piping Type: Uponor helioPEX X2 tubing.

        - Pre-insulated Supply and Return Piping Type: Uponor Ecoflex®.

  - ACCESSORIES

    - Water Temperature and HVAC Controls: Refer to the controls section of the tender document.

    - Thermostats: Thermostats shall be of type designed specifically for Radiant Heating and shall have slab sensing capability. Thermostats shall be supplied by PEX tubing manufacturer.

[Select one thermostat type in “.1” below]

      - Thermostat Type: Uponor Heat-only Thermostat with Touchscreen.

      - Thermostat Type: Uponor SetPoint 521, Programmable Thermostat with floor sensor.

      - Thermostat Type: Uponor Smatrix Pulse Digital Thermostat (T-169) [must be used with Smatrix Pulse Controller (X-265)].

    - Loop Valve Actuators: Individual loop actuators shall be thermally actuated for quiet operation. Valve actuators shall be supplied by PEX tubing manufacturer.

    - Zone Control Panels: Zone control panels with LED lights indicating zone operational status shall be provided for each manifold location or Smatrix Pulse Controller (X-265). Zone control panels shall be supplied by PEX tubing manufacturer.

    - Manifold Cabinets: All manifolds shall be mounted in a surface mounted or recessed metal cabinet. The cabinet shall be lockable and be able to be painted. The cabinets shall be supplied by the PEX tubing manufacturer.

    - Shut-Off Valves: Shut-Off valves shall be supplied by the PEX tubing manufacturer.

    - Horizontal Pipe Support Channels: All horizontal pipe supports for PEX sizes 1/2 inch and greater shall be gauge 23 galvanized steel channels and be supplied by the PEX tubing manufacturer.

      - Pipe Support Type: Uponor PEX-a Pipe Support.

  - RELATED MATERIALS

    - Related Materials: Refer to other sections listed in Related Sections paragraph herein for related materials.

- EXECUTION

  - MANUFACTURER’S INSTRUCTIONS

    - Compliance: Comply with manufacturer’s product data, including product technical bulletins, installation instructions and product packaging instructions for installation.

  - EXAMINATION

    - Site Verification of Conditions: Verify substrate conditions which have been previously installed under other sections, are acceptable for installation in accordance with manufacturer’s instructions.

  - INSTALLATION

    - Radiant Heating and Cooling Installation:

      - Install hydronic radiant heat and cooling tubing loops in accordance with tubing manufacturer’s recommendations and as indicated on Contract Drawings. Installation shall follow shop drawings for tube layout, tube spacing, manifold configuration, and manifold location. Comply with notes on shop drawings.

      - Manifolds supply and return piping shall be isolated with ball valves.

      - Fittings and manifolds shall be accessible for maintenance. The only exceptions are for repair splice with manufacturer’s approved fittings and procedure for concealed connections.

      - Install tubing loops without splices. It is acceptable to install a repair splice within the embedded loop should on-site damage occur and an emergency repair be authorized. Refer to PEX tubing manufacturer’s installation handbook for instructions on the proper installation of the repair splice.

      - Ensure that no glues, solvents, sealants or chemicals come in contact with the tubing without prior permission from the tube manufacturer.

      - Manufacturer’s bend supports shall be used where tubing enters and exits the slab.

      - Methods of tubing attachment shall be to manufacturer’s installation handbook.

      - Pressurize tubing system with air or water in accordance with applicable codes and manufacturer's recommendations.

      - Comply with safety precautions when pressure testing, including use of compressed air, where applicable. Water shall not be used to pressurize the system if ambient air temperature has the possibility of dropping below 32°F (0°C).

      - Ensure system to be protected from freezing conditions.

      - Initial Balancing: Adjust flow to all loops as indicated on shop drawings. Flow adjustment settings are to be generated by the Uponor LoopCAD software.

      - System shall not be operated during panel concrete curing period unless permission has been granted and specific instructions on panel pre-heating has been provided.

    - Related Products Installation: Refer to other sections listed in Related Sections paragraph herein for related products installation.

  - FIELD QUALITY REQUIREMENTS

    - Site Tests (Installation and Post-Installation Testing): [Specify applicable test requirements to be performed during and after product installation].

    - Manufacturer’s Field Services: Provide manufacturer’s field service consisting of product use recommendations and periodic site visit for inspection of product installation in accordance with manufacturer’s instructions.

      - Site Visits: [Specify number and duration of periodic site visits].

  - ADJUSTING

    - Adjusting: Balance all loops by adjusting flowmeter to the desired setting according to LoopCAD design or designer recommendation.

    - Adjusting: Balance all hydronic distribution lines based on manifold or terminal unit requirement.

  - CLEANING

    - Cleaning: Remove temporary coverings and protection of adjacent work areas. Repair or replace damaged installed products. Clean installed products in accordance with manufacturer’s instructions prior to Owner’s acceptance. Remove construction debris from project site and legally dispose of debris. If a chemical disinfection product is used, care must be given to either isolate the PEX from the rest of the system or use a procedure recommended by the manufacturer.

  - PROTECTION

    - Protection: Protect installed product and finish surfaces from damage during construction.

### END OF SECTION