Uponor Ltd.

2000 Argentia Road

Plaza 1, Suite 200

Mississauga, ON L5N 1W1

888.994.7726

www.uponorpro.com

## SECTION 23 21 13

### FLOOR-HEATING AND COOLING EQUIPMENT

1.0	 General

  - SUMMARY

.1	Section Includes: Hydronic radiant floor heating and cooling distribution system.

.1	Provide labour, materials, transportation, equipment and services to install a hydronic radiant floor and cooling system where indicated on the Contract Drawing and specified herein.

.2	Related Sections:

.1	Examine all other portions of the subcontract documents for work or other terms and conditions related to the work of this section.

.2	Provide all work hereunder as required for the support and accommodation of related work.

  - REFERENCES

.1	General: Standards listed by reference, including revisions by issuing authority, form part of this specification section to extent indicated. Standards listed are identified by issuing authority, authority abbreviation, designation number, title, or other designation established by issuing authority. Standards subsequently referenced herein are referred to by issuing authority abbreviation and standard designation.

.2	American Society for Testing and Materials (ASTM):

.1	ASTM F876 Standard Specification for Cross-Linked Polyethylene (PEX) Tubing.

.2	ASTM F877 Standard Specification for Cross-Linked Polyethylene (PEX).Plastic Hot and Cold Water Distribution Systems.

.3	ASTM F2788 Standard Specification for Metric-Sized PEX Pipe.

.4	ASTM F1960 Standard Specification for Cold Expansion Fittings with PEX Reinforcing Rings for Use with Cross-Linked Polyethylene (PEX) Tubing.

.3	Underwriters’ Laboratories of Canada Inc:

.1	CAN/ULC-S101 Standard Methods of Fire Endurance Tests of Building Construction and Materials.

.2	CAN/ULC-S115 Standard Method of Fire Tests of Firestop Systems.

.3	CAN/ULC-S102.2 Standard for Surface Burning Characteristics of Flooring, Floor Covering and Miscellaneous Materials and Assemblies.

.4	Canadian Standards Association (CSA):

.1	CAN/CSA B137.5 Cross-Linked Polyethylene (PEX) for Pressure Applications.

.2	CAN/CSA B214 Installation Code for Hydronic Heating Systems.

.5	German Institute of Standards (DIN):

1.	DIN 4726 Warm Water Floor Heating Systems and Radiator Connections – Piping Made Out of Plastic Materials.

.6	Plastic Pipe Institute (PPI):

- PPI Technical Report TR-4.

.7	Uponor, Complete Design Assistance Manual (CDAM), current edition.

.8	Uponor, Advanced Design Suite Software.

.9	Uponor, Installation Handbook, Radiant Floor, current edition.

  - SYSTEM DESCRIPTION

.1	Performance Requirements: Provide hydronic radiant floor heating and cooling system which has been manufactured, fabricated and installed to comply with regulatory agencies and to maintain performance criteria stated by manufacturer without defects, damage or failure. The floor loop design shall be capable of providing the specified heating and cooling loads without altering the flow output of the specified circulators.

  - SUBMITTALS

.1	General: Submit listed submittals in accordance with Conditions of the Contract and Division 1 Submittal Procedures Section.

.2	Product Data: Submit product data for specified products.

.1	Submit verification of Standard Grade hydrostatic pressure ratings from Plastic Pipe Institute in accordance with TR-4. The following 3 Standard Grade ratings are required: 200 degrees F (93 degrees C) at 80 psi (551 kPa); 180 degrees F (82 degrees C) at 100 psi (689 kPa) and 73.4 degrees F (23 degrees C) at 160 psi (1102 kPa).

.2	Submit Product Submittal sheets for tubing, manifolds, connection system, loop and/or manifold actuators, thermostats and zone controls.

.3	Performance Data: Submit manufacturer’s design calculations showing compliance with meeting heat and cooling loads based on maximum  [specify] °F average heating supply water and maximum [specify] °F entering cooling supply water. Additional design calculations shall include:

.1	Flowrate in each loop

.2	Head loss in each loop

.3	Surface temperature(s)

.4	Loop design temperature drop(s)

.5	Loop spacing(s)

.6	Loop length(s)

.4	Regulatory Listings: Submit applicable UL, ULC, Warnock Hersey, Intertek or QAI and CSA or NSF listings as proof of compliance with Federal, Provincial and Municipal building codes. Listings shall include the following.

.1	Submit listings that indicate that the PEX-a tubing system has been listed to CAN/ULC-S101 when the PEX-a tubing is incorporated in and traverses a CAN/ULC-S101 floor/ceiling assembly. The listings must be appropriate to assemblies on site.

.2	Submit listings that indicate that the PEX-a tubing firestop system has been listed to CAN/ULC-S115 when the PEX-a tubing penetrates a fire separation. The listings must be appropriate to assemblies on site.

.3	Submit listings that indicate that the PEX-a tubing has been listed to CAN/ULC-S102.2 for maximum 25 flame spread and maximum 50 smoke developed.

.5	Shop Drawings: Submit design print-out of Uponor Advanced Design Suite and shop drawings indicating loop layout, manifold locations, initial loop flow balance settings, floor profiles, floor coverings and product components, including anchorage, accessories and finishes.

.1	Include installation drawings of tubing layout indicating loop length, loop spacing, tube size and detail notes to aid in installation of system.

.2	No fabrication shall be performed until approval is given.

.6	Quality Assurance Submittals: Submit the following:

.1	Copy of certificate indicating that the installer is certified in the installation of the manufacturer’s products.

.2	Manufacturer’s Instructions: Manufacturer’s installation instructions.

.3	Installer shall provide in writing to the project owner that the PEX-a tubing and components furnished under this specification conforms to the material and mechanical requirements specified herein.

.7	Closeout Submittals: Submit the following:

.1	Operation and Maintenance Data: Operation and maintenance data for installed products in accordance with Division 1 Closeout Submittals (Maintenance Data and Operation Data) Section including methods for maintaining installed products and precautions against cleaning materials and methods detrimental to finishes and performance.

.2	Warranty: Warranty documents specified herein.

.3	Manufacturer’s Field Reports: Manufacturer’s field reports specified herein.

.4	Final “As-Built” loop layout drawing.

.5	Copy of Uponor Advanced Design Suite software printout.

.6	Record Documents: Project record documents for installed materials in accordance with Division 1 Closeout Submittals (Project Record Documents) Section.

  - QUALITY ASSURANCE

.1	Qualifications:

.1	Installer Qualifications: Installer shall be experienced in performing work of this section and has specialized in installation of work similar to that required for this project.

.2	Installation Qualifications: Installation must be by skilled tradesmen holding a trade qualification license or apprentices under the supervision of a licensed tradesman.

.3	Installer Qualifications: Installer must be recognized by the manufacturer as a “Trained Installer”.

.2	Regulatory Requirements: PEX-a tubing and components shall be installed in full compliance with all Federal, Provincial and Municipal codes, standards and requirements. In particular:

.1	PEX-a tubing shall be listed to a maximum 25 flame spread and maximum of 50 smoke developed per the requirements of CAN/ULC-S102.2.

.2	PEX-a tubing penetrating a fire separation shall be sealed per CAN/ULC-S115.

.3	PEX-a tubing contained within a CAN/ULC-S101 floor/ceiling assembly shall be listed per CAN/ULC-S101.

.3	Pre-installation Meetings: Conduct pre-installation meeting to verify project requirements, substrate conditions, floor coverings, manufacturer’s installation instructions and manufacturer’s warranty requirements. Comply with Division 1 Project Management and Coordination (Project Meetings) Section.

  - DELIVERY, STORAGE AND HANDLING

.1	General: Comply with Division 1 Product Requirements Sections.

.2	Ordering: Comply with manufacturer’s ordering instructions and lead-time requirements to avoid construction delays.

.3	Delivery: Deliver materials to job site in manufacturer’s original, unopened, undamaged containers with identification labels intact.

.4	Storage and Protection: Store materials protected from exposure to harmful weather and job site conditions.

.1	Store PEX-a tubing in original packaging or under cover to avoid dirt or foreign material from being introduced into the tubing.

.2	Do not expose PEX-a tubing to direct sunlight for more than 30 days. If construction delays are encountered, installer is responsible for providing cover to portions of tubing exposed to direct sunlight.

  - WARRANTY

.1	Project Warranty: Refer to Conditions of the Contract for project warranty provisions.

.2	PEX Manufacturer’s Warranty: Warranty must meet the following conditions:

.1	PEX-a tubing shall carry a 25-year non-prorated warranty against failure due to defect in material or workmanship and;

.2	Manifolds and fittings shall carry a 5-year non-prorated warranty against failure due to defect in material or workmanship and;

.3	Controls and electrical components shall carry a 2-year non-prorated warranty against failure due to defect in material or workmanship and;

.4	Warranty shall provide for repair or replacement of any tube or fittings which are proven to be defective and pay for consequential damages and;

.5	Warranty shall be transferable to subsequent owners and;

.6	Effective Warranty: Current manufacturer’s warranty at time of installation and;

.7	Warranty Period: Warranty shall commence on Date of Substantial Completion.

  - SYSTEM STARTUP AND OWNER’S INSTRUCTION

.1	System Startup: [Specify system startup requirements].

.2	Owner’s Instruction: Instruct Owner’s personnel in operation and maintenance of installed units. Provide manufacturer’s installation, operation and maintenance instructions for installed units.

- Products

2.1	RADIANT FLOOR HEATING SYSTEM

.1	Manufacturer: Uponor Ltd.

.2	Proprietary System: Uponor hePEX Radiant Panel Heating System.

  - PRODUCT SUBSTITUTIONS

.1	Substitutions: No substitutions permitted.

  - MATERIALS

.1	Tube Materials: Tube shall be cross-linked polyethylene (PEX) manufactured by PEX-a or peroxide method.

.1	Tubing Type: Wirsbo hePEX tubing.

.2	Oxygen Barrier: Tube shall have an oxygen barrier capable of limiting oxygen migration through the tube wall to no greater than 0.10 g/m3/day at 104 degree F (40 degrees C) water temperature per the requirements of DIN 4726.

.3	PEX-a tubing shall be CSA B137.5 listed for both hydronic and potable water distribution systems.

.4	PEX-a tubing shall be manufactured in accordance with ASTM F876 and ASTM F877. The tube shall be listed to ASTM by an independent third party agency.

.5	PEX-a tubing shall be ASTM F876 tested and approved for excessive temperature and pressure for 725 hours @ 210 degrees F (99 degrees C) at 150 psi (1035 kPa).

.6	PEX-a tubing shall have Standard Grade hydrostatic design and pressure ratings of 200 F (82 degrees C) at 80 psi (551 kPa), 180 degrees F (82 degrees C) at 100 psi (689 kPA), and 73.4 degrees F (23 degrees C) at 160 psi (1102 kPa). Temperature and pressure ratings shall be issued by the Plastic Pipe Institute (PPI), a division of the Society of the Plastic Industry (SPI).

.7	Minimum bend radius for cold bending of the PEX-a tubing shall not be less than 6 times the outside diameter. Bends with a radius less than stated shall require the use of a bend support as supplied by tube manufacturer.

.8	PEX-a tubing dimensions shall be: [specify one dimension below]

.1	1/2” nominal inside diameter in accordance with ASTM F876.

.1	5/8” nominal inside diameter in accordance with ASTM F876.

.1	3/4” nominal inside diameter in accordance with ASTM F876.

.1	1” nominal inside diameter in accordance with ASTM F876.

[Select one manifold type below in “.2” below. Engineered Polymer (EP) manifold c/w visual loop flow meters, max.15.4 gpm for 8-loop manifold; TruFLOW Junior (Brass), max. 14 gpm for 8-loop manifold; TruFLOW Classic, max. 21 gpm for 12-loop manifold; Stainless-steel Manifold Assembly, 1” with Flow Meter, max. 14 gpm for 12-loop manifold; Stainless-steel Manifold Assembly, 1-1/4” with Flow Meter, max. 21 gpm for 12-loop manifold]

.2	Manifold Materials: Engineered Polymer (EP) manifold shall be fully assembled and mounted on a durable bracket with air vents and drains on both the supply and return manifold sections. Manifold shall be designed to handle maximum 15.4 gpm on 8-loop manifold. Manifold shall have R32 unions on the inlet side of the manifold to allow for various connection adapters. Visual flow meters shall be pre-mounted on the manifold assembly. Manifold shall be capable of full flow isolation on each loop.

.1	Manifold Type: Uponor Engineered Polymer (EP) Manifold.

.2	Manifolds shall be supplied by the PEX-a tubing manufacturer.

.3	Manifolds shall have integral manual air vents on supply and return

.4	Manifolds shall be manufactured from Engineered Polymer (EP).

.5	Manifolds shall be supplied with manufacturers mounting brackets.

.6	Manifolds shall be pre-assembled with visual flow indicators.

.2	Manifold Materials: Brass manifold shall be fully assembled and mounted on a durable bracket with air vent and drain on the return manifold sections. Manifold shall be designed to handle maximum 14 gpm for 8-loop manifold. Manifold shall have R32 unions on the inlet side of the manifold to allow for various connection adapters. Manifold shall be capable of full flow isolation on each loop.

.1	Manifold Type: Uponor TruFLOW Junior manifold.

.2	Manifolds shall be supplied by the PEX-a tubing manufacturer.

.3	Manifolds shall have integral manual air vent and drain on the return manifold.

.4	Manifolds shall be manufactured from brass

.5	Manifolds shall be supplied with manufacturers mounting brackets.

.6	Manifolds shall 1” internal barrel diameter.

.2	Manifold Materials: Brass manifold shall be fully assembled and mounted on a durable bracket with air vent and drain on the return manifold sections. Manifold shall be designed to handle maximum 21 gpm for 12-loop manifold. Manifold shall have R32 unions on the inlet side of the manifold to allow for various connection adapters. Manifold shall be capable of full flow isolation on each loop.

.1	Manifold Type: Uponor TruFLOW Classic manifold.

.2	Manifolds shall be supplied by the PEX-a tubing manufacturer.

.3	Manifolds shall have integral manual air vent and drain on the return manifold.

.4	Manifolds shall be manufactured from brass

.5	Manifolds shall be supplied with manufacturers mounting brackets.

.6	Manifolds shall 1-1/4” internal barrel diameter.

.2	Manifold Materials: Stainless Steel manifold shall be fully assembled and mounted on a durable bracket. Manifold shall come fully assembled with air vent and drain on both the supply and return manifold sections, visual loop flow meters and isolation ball valves. Manifold shall be designed to handle maximum 14 gpm for 12-loop manifold. Manifold shall be capable of full flow isolation on each loop.

.1	Manifold Type: Stainless-steel Manifold Assembly, 1” with Flow Meter.

.2	Manifolds shall be supplied by the PEX-a tubing manufacturer.

.3	Manifolds shall have integral manual air vent and drain on both the supply and return manifold.

.4	Manifolds shall be manufactured from stainless steel.

.5	Manifolds shall be supplied with manufacturers mounting brackets.

.6	Manifolds shall be pre-assembled with visual loop flow indicators.

.7	Manifolds shall be pre-assembled with isolation ball valves.

.8	Manifolds shall 1” internal barrel diameter.

.2	Manifold Materials: Stainless Steel manifold shall be fully assembled and mounted on a durable bracket. Manifold shall come fully assembled with air vent and drain on both the supply and return manifold sections, visual loop flow meters and isolation ball valves. Manifold shall be designed to handle maximum 21 gpm for 12-loop manifold. Manifold shall be capable of full flow isolation on each loop.

.1	Manifold Type: Stainless-steel Manifold Assembly, 1-1/4” with Flow Meter.

.2	Manifolds shall be supplied by the PEX-a tubing manufacturer.

.3	Manifolds shall have integral manual air vent and drain on both the supply and return manifold.

.4	Manifolds shall be manufactured from stainless steel.

.5	Manifolds shall be supplied with manufacturers mounting brackets.

.6	Manifolds shall be pre-assembled with visual loop flow indicators.

.7	Manifolds shall be pre-assembled with isolation ball valves.

.8	Manifolds shall 1” internal barrel diameter.

.3	Manifold Isolation Ball Valves [EP and TruFLOW manifolds only]: Manifolds shall be isolated at the inlet and outlet of the manifold with full flow ball valves. The supply ball valve shall have an internal strainer.

.1	Isolation Ball Valve Type: Uponor supply and return ball valves.

.2	Isolation ball valves shall be supplied by the PEX-a tubing manufacturer.

.4	Fitting Materials: Fittings shall be manufactured of polysulfone or dezincification resistant brass. Fittings shall be nose cone insert type compression fitting, nose cone insert type swivel fitting or PEX-a cold expansion type fitting.

.1	Fittings shall be supplied by the PEX-a tubing manufacturer.

.2	Compression fitting shall be an assembly consisting of nose cone insert, compression ring and compression nut.

.3	Swivel fitting shall be an assembly consisting of nose cone insert, swivel nut and PEX-a cold expansion ring.

.4	PEX-a cold expansion type fitting shall be an assembly consisting of insert and PEX-a cold expansion ring.

.5	Supply and Return Piping to Manifolds: Piping run in heated spaces shall be cross-linked tubing with oxygen diffusion barrier capable of limiting oxygen migration through the tube wall to no greater than 0.10 g/m3/day at 104 degrees F (40 degrees C) water temperature per the requirements of DIN 4726. Supply and return piping run underground shall be cross-linked tube encased in a pre-insulated polyethylene corrugated jacket.

.1	Supply and Return Piping Type: Wirsbo HePEX tubing

.2	Pre-insulated Supply and Return Piping Type: Uponor Ecoflex

  - ACCESSORIES

.1	Water Temperature and HVAC Controls: Refer to the controls section of the tender document.

[Select one thermostat type in “.2” below]

.2	Thermostats: Thermostats shall be of type designed specifically for Radiant Floor Heating and shall have slab sensing capability. Thermostats shall be supplied by PEX-a tubing manufacturer.

.1	Thermostat Type: Uponor heat-only thermostat

.1	Thermostat Type: Uponor heat and cool thermostat.

.1	Thermostat Type: Uponor 501 single stage controller.

.1	Thermostat Type: Uponor 501s single stage controller with slab sensor.

.1	Thermostat Type: Uponor 511s programmable single stage controller with slab sensor.

.1	Thermostat Type: Uponor 512 programmable two-stage controller.

.3	Loop Valve Actuators: Individual loop actuators shall be thermally actuated for quiet operation. Valve actuators shall be supplied by PEX-a tubing manufacturer.

.4	Zone Control Panels: Zone control panels with LED lights indicating zone operational status shall be provided for each manifold location. Zone control panels shall be supplied by PEX-a tubing manufacturer.

.5	Manifold Cabinets: All manifolds shall be mounted in a recessed metal cabinet. The cabinet shall be lockable and be able to be painted. The cabinets shall be supplied by the PEX-a tubing manufacturer.

2.5	RELATED MATERIALS

.1	Related Materials: Refer to other sections listed in Related Sections paragraph herein for related materials.

3.0	 Execution

  - MANUFACTURER’S INSTRUCTIONS

.1	Compliance: Comply with manufacturer’s product data, including product technical bulletins, installation instructions and product packaging instructions for installation.

  - EXAMINATION

.1	Site Verification of Conditions: Verify substrate conditions which have been previously installed under other sections, are acceptable for installation in accordance with manufacturer’s instructions.

  - INSTALLATION

.1	Radiant Heating and Cooling Installation:

.1	Install hydronic radiant heat and cooling tubing loops in accordance with tubing manufacturer’s recommendations and as indicated on Contract Drawings. Installation shall follow shop drawings for tube layout, tube spacing, manifold configuration, and manifold location. Comply with notes on shop drawings.

.2	Manifolds supply and return piping shall be isolated with ball valves.

.3	Fittings and manifolds shall be accessible for maintenance. The only exceptions are for repair splice with manufacturer’s approved fittings and procedure for concealed connections.

.4	Install tubing loops without splices. It is acceptable to install a repair splice within the embedded loop should on-site damage occur and an emergency repair be authorized. Refer to PEX-a tubing manufacturer’s installation handbook for instructions on the proper installation of the repair splice.

.5	Ensure that no glues, solvents, sealants or chemicals come in contact with the tubing without prior permission from the tube manufacturer.

.6	Manufacturer’s bend supports shall be used where tubing enters and exits the slab.

.7	Methods of tubing attachment shall be to manufacturer’s installation handbook.

.8	Pressurize tubing system with air or water in accordance with applicable codes or, in the absence of applicable codes, to a pressure of 60 psi (413 kPa) for 24 hours prior to encasement of tubing system. Tubing shall remain pressurized during encasement and for a period of 24 hours thereafter to ensure system integrity.

.9	Comply with safety precautions when pressure testing, including use of compressed air, where applicable. Water shall not be used to pressurize the system if ambient air temperature has the possibility of dropping below 32 degrees F (0 degrees C).

.10	Ensure system is freeze proof should ambient air temperature be anticipated to drop below 32 degrees F (0 degrees C) and the system is not under full operation.

.11	Initial Balancing: Adjust flow to all loops as indicated on shop drawings. Flow adjustment settings are to be generated by the Uponor Advanced Design Suite software.

.12	System shall not be operated during panel concrete curing period unless permission has been granted and specific instructions on panel pre-heating has been provided.

.2	Related Products Installation: Refer to other sections listed in Related Sections paragraph herein for related products installation.

  - FIELD QUALITY REQUIREMENTS

.1	Site Tests (Installation and Post-Installation Testing): [Specify applicable test requirements to be preformed during and after product installation].

.2	Manufacturer’s Field Services: Provide manufacturer’s field service consisting of product use recommendations and periodic site visit for inspection of product installation in accordance with manufacturer’s instructions.

.1	Site Visits: [Specify number and duration of periodic site visits].

  - ADJUSTING

.1	Adjusting: Balance all loops to equal temperature drops after radiant floor heating system has been in operation and building temperature has stabilized to normal operating conditions.

  - CLEANING

.1	Cleaning: Remove temporary coverings and protection of adjacent work areas. Repair or replace damaged installed products. Clean installed products in accordance with manufacturer’s instructions prior to Owner’s acceptance. Remove construction debris from project site and legally dispose of debris.

  - PROTECTION

.1	Protection: Protect installed product and finish surfaces from damage during construction.

### END OF SECTION