GF Building Flow Solutions

6510 Kennedy Road

Mississauga, ON L5T 2X4

888 994 7726

www.uponor.ca

## Section 22 11 16

### DOMESTIC WATER PIPING

- GENERAL

  - SECTION INCLUDES

    - Domestic water piping and fittings for the following applications:

      - Domestic cold-water piping

      - Domestic hot-water piping

      - Domestic hot-water recirculation piping

  - RELATED SECTIONS

    - Section 22 11 13 – Facility Water Distribution Piping

    - Section 22 07 19 – Plumbing Piping Insulation

    - Section 22 05 23 – General-Duty Valves for Plumbing Piping

    - Section 22 05 29 – Hangers and Supports for Plumbing Piping and Equipment

  - REFERENCES

    - General: Standards listed by reference, including revisions by issuing authority, form part of this specification section to extent indicated. Standards listed are identified by issuing authority, authority abbreviation, designation number, title, or other designation established by issuing authority. Standards subsequently referenced herein are referred to by issuing authority abbreviation and standard designation.

    - American Society for Testing and Materials (ASTM):

      - ASTM F876 Standard Specification for Cross-Linked Polyethylene (PEX) Tubing.

      - ASTM F877 Standard Specification for Cross-Linked Polyethylene (PEX) Plastic Hot and Cold Water Distribution Systems.

      - ASTM F1960 Standard Specification for Cold Expansion Fittings with PEX Reinforcing Rings for Use with Cross-Linked Polyethylene (PEX) Tubing.

    - Canadian Standards Association (CSA):

      - CAN/CSA B137.5 Cross-Linked Polyethylene (PEX) Tubing Systems for Pressure Applications.

    - National Sanitation Foundation (NSF):

      - NSF/ANSI 14 Plastic Piping System Components and Related Materials

      - NSF/ANSI 61 Drinking Water System Components – Health Effects.

    - Underwriters’ Laboratories of Canada Inc:

      - CAN/ULC-S101 Standard Methods of Fire Endurance Tests of Building Construction and Materials.

      - CAN/ULC-S115 Standard Method of Fire Tests of Firestop Systems.

      - CAN/ULC-S102.2 Standard for Surface Burning Characteristics of Flooring, Floor Covering and Miscellaneous Materials and Assemblies.

    - Plastics Pipe Institute (PPI):

      - PPI Technical Report TR-4.

    - GF Building Flow Solutions (Uponor):

      - Uponor PEX Piping Systems Installation Guide, current edition.

      - Uponor PEX Piping Systems Design and Installation Manual, current edition.

  - SYSTEM DESCRIPTION

    - Performance Requirements: Provide PEX tubing potable water distribution system which has been manufactured, fabricated, and installed to comply with Federal, Provincial, and Municipal plumbing and building codes and to maintain performance criteria stated by manufacturer without defects, damage, or failure.

  - SUBMITTALS

    - General: Submit listed submittals in accordance with Conditions of the Contract and Division 1 Submittal Procedures Section.

    - Product Data: Submit product data for specified products.

      - Submit verification of Standard Grade hydrostatic pressure ratings from Plastic Pipe Institute in accordance with TR-4. The following 3 Standard Grade ratings are required:

        - 200°F (93°C) at 80 psi (551 kPa).

        - 180°F (82°C) at 100 psi (689 kPa).

        - 73°F (23°C) at 160 psi (1102 kPa).

      - Submit Product Submittal sheets for tubing, manifolds, brackets, pre-sleeved tubing, pre-insulated tubing, supports, tubing/fitting connection system, valves, and fittings.

    - Regulatory Listings: Submit applicable UL, ULC, Warnock Hersey, Intertek or QAI and CSA or NSF listings as proof of compliance with Federal, Provincial and Municipal plumbing and building codes.

      - Submit listings that indicate that the PEX tubing system has been listed to CAN/ULC-S101 when the PEX tubing is incorporated in and traverses a CAN/ULC-S101 floor/ceiling assembly and wall assembly. The listing must be appropriate to assemblies on site.

      - Submit listings that indicate that the PEX tubing firestop system has been listed to CAN/ULC-S115 where the PEX tubing penetrates a fire separation. The listing must be appropriate to assemblies on site.

      - Submit listings that indicate that the PEX tubing system has been listed to CAN/ULC-S102.2 for maximum 25 flame spread and maximum 50 smoke developed.

      - Submit listings that indicate that the PEX tubing system has been listed to CAN/CSA-B137.5.

    - Quality Assurance Submittals: Submit the following:

      - Copy of manufacturer’s letter indicating that the installer has been recognized by the manufacturer as a “Trained Installer” trained in the use of its PEX tubing potable water distribution system.

      - Manufacturer’s Instructions: Manufacturer’s installation instructions.

      - Installer shall provide in writing to the project owner that the PEX tubing and components furnished under this specification conforms to the material and mechanical requirements specified herein.

      - Installer shall provide manufacturer’s letter that any firestop coming in contact with the PEX tubing is chemically compatible with the PEX tubing.

      - Submit the listing that the PEX tubing, PEX rings, and PEX fittings from the same manufacturer have been tested together.

    - Closeout Submittals: Submit the following:

      - Warranty: Warranty documents specified herein.

      - Manufacturer’s Field Reports: Manufacturer’s field reports specified herein.

      - Record Documents: Project record documents for installed materials in accordance with Division 1 Closeout Submittals (Project Record Documents) Section.

  - QUALITY ASSURANCE

    - Qualifications:

      - Installer Qualifications: Use an installer with demonstrated experience on projects of similar size and complexity and who has been trained by GF Building Flow Solutions (Uponor) or an Uponor-approved trainer.

        - Certifications: Provide letters of certification indicating: Installer uses skilled workers holding a trade qualification license or equivalent, or apprentices under the supervision of a licensed tradesperson.

        - If PEX-a is used as an approved alternate for applications where metallic piping is the basis of design the manufacturer shall submit shop drawings clearly indicating that the design has been analyzed and modified, as required, to maintain required pressure and flow. Any design resulting in reduced system pressure as a result of improper PEX-a sizing or design shall not be permitted.

    - Regulatory Requirements: PEX tubing and components shall be installed in full compliance with all Federal, Provincial and Municipal codes, standards, and requirements. In particular:

      - PEX tubing shall be listed to a maximum 25 flame spread and maximum of 50 smoke developed per the requirements of CAN/ULC-S102.2.

        - As outlined in CAN/ULC S102 Appendix Section A1.23, Plastic Fittings and Valves, fittings shall be tested and listed by being mounted to plastic pipe in a method that is representative of field installation.

        - Uponor PEX piping manufactured with a maximum nominal OD of 3 inch (80 mm) and encased in 1/2 inch insulation in accordance with Table 3-5 shall have no limitation on spacing (see PEX Piping Systems Design and Installation Manual).

        - Up to and including 2 inch (50 mm) Uponor PEX-a (waterfilled, uninsulated); adjacent runs of waterfilled, uninsulated piping in a return-air plenum have no spacing limitations.

      - CAN/ULC S115:

        - PEX tubing penetrating a fire separation shall be sealed per 
CAN/ULC-S115.

      - CAN/ULC S101:

        - PEX tubing contained within a fire separation shall be listed per CAN/ULC-S101.

        - Ice maker & laundry boxes when contained within a fire separation shall be listed as part of the assembly to CAN/ULC S101.

    - Pre-installation Meetings: Conduct pre-installation meeting to verify project requirements, manufacturer’s installation instructions, and manufacturer’s warranty requirements. Comply with Division 1 Project Management and Coordination (Project Meetings) Section.

    - All calculations are performed with Uponor ProPEX® ASTM F1960 fittings. Contractor must provide report with calculations if using other fitting type to make sure different flow characteristics are accounted for.

  - DELIVERY, STORAGE, AND HANDLING

    - General: Comply with Division 1 Product Requirements Sections.

    - Ordering: Comply with manufacturer’s ordering instructions and lead-time requirements to avoid construction delays.

    - Delivery: Deliver materials to job site in manufacturer’s original, unopened, undamaged containers with identification labels intact.

    - Storage and Protection: Store materials protected from exposure to harmful weather and job site conditions.

      - Store PEX tubing in original packaging or under cover to avoid dirt or foreign material from being introduced into the tubing and protect tubing from UV generating lights.

      - Do not expose white PEX tubing to direct sunlight or near UV light sources for more than 30 days, do not expose red and blue PEX tubing to direct sunlight or near UV light sources for more than 6 months. If construction delays are encountered, installer is responsible for providing UV protection to portions of tubing exposed to direct sunlight.

  - WARRANTY

    - Project Warranty: Refer to Conditions of the Contract for project warranty provisions.

    - PEX Manufacturer’s Warranty: Warranty must meet the following conditions:

      - AquaPEX® tubing and ProPEX fittings shall carry a twenty-five (25) year warranty when used with all Uponor products, non-prorated warranty against failure due to defect in material or workmanship and;

      - All tubing manufacturer’s valves and stops shall carry a five (5) year non-prorated warranty against failure due to defect in material or workmanship and;

      - The assembly of manufacturer’s tubing, fittings, and rings shall carry a 
twenty-five (25) year non-prorated warranty on maintaining a leak-proof seal and;

      - Warranty when using non-Uponor products:

        - AquaPEX tubing shall be ten (10) years from twenty-five (25) years system warranty when using fittings from other manufacturers.

        - ProPEX fittings shall be one (1) year from twenty-five (25) years system warranty when using pipe from other manufacturers.

      - Warranty shall provide for repair or replacement of any tube, fittings, or connection, which are proven to be defective and pay for consequential damages and;

      - Warranty shall be transferable to subsequent owners and;

      - Effective Warranty: Current manufacturer’s warranty at time of installation and;

      - Warranty Period: Warranty shall commence on date the products are installed.

- PRODUCTS AND MATERIALS

  - MANUFACTURERS

    - Acceptable manufacturer: GF Building Flow Solutions (Uponor Ltd.), located at: 
6510 Kennedy Road; Mississauga, ON, L5T 2X4; tel: 888 994 7726
email: naspecifications@georgfischer.com; web: www.uponor.ca

      - All PEX tubing, fittings, and fitting assemblies shall be by one manufacturer.

      - All PEX tubing, PEX rings, and PEX fittings from the same manufacturer have been tested together and certified as a system.

  - PRODUCT SUBSTITUTIONS

    - Substitutions: No substitutions permitted.

    - Requests for substitutions will be considered in accordance with provisions of Section 01 60 00 – Product Requirements.

  - DOMESTIC WATER PIPING AND FITTINGS

    - Performance requirements:

      - PEX tubing shall be ASTM F876 tested and approved for excessive temperature and pressure for 725 hours at 210°F (99°C) at 150 psi (1035 kPa).

      - PEX tubing shall be manufactured in accordance with ASTM F876, ASTM F877 and CAN/CSA-B137.5. The tube shall be listed to ASTM by an independent third party agency.

      - PEX tubing shall be listed to both NSF/ANSI 14 and 61.

      - Temperature and pressure ratings shall be issued by the Plastics Pipe Institute (PPI), a division of the Society of the Plastic Industry (SPI). PEX tubing shall have Standard Grade hydrostatic design and pressure ratings of:

        - 200°F (82°C) at 80 psi (551 kPa).

        - 180°F (82°C) at 100 psi (689 kPa).

        - 73°F (23°C) at 160 psi (1102 kPa).

      - Minimum bend radius for cold bending of the PEX tubing shall not be less than six (6) times the outside diameter. Bends with a radius less than stated shall require the use of a bend support as supplied by tube manufacturer.

      - PEX-a piping shall be tested to comply with the ASTM F2023 requirement for minimum chlorine resistance at the end use condition of 100% of the time at 140°F (60°C) at 80 psi (551 kPa) gauge pressure.

        - PEX-a piping and tubing material designation codes shall be PEX 5106 for white pipe or PEX 5306 for red and blue pipe.

      - PEX tube dimensions shall be:

        - 1/2 inch (15 mm) nominal inside diameter in accordance with ASTM F876 and ASTM F877.

        - 3/4 inch (20 mm) nominal inside diameter in accordance with ASTM F876 and ASTM F877.

        - 1 inch (25 mm) nominal inside diameter in accordance with ASTM F876 and ASTM F877.

        - 1-1/4 inch (32 mm) nominal inside diameter in accordance with ASTM F876 and ASTM F877.

        - 1-1/2 inch (40 mm) nominal inside diameter in accordance with ASTM F876 and ASTM F877.

        - 2 inch (50 mm) nominal inside diameter in accordance with ASTM F876 and ASTM F877.

        - 3 inch (80 mm) nominal inside diameter in accordance with ASTM F876 and ASTM F877.

    - Piping:

      - Uponor AquaPEX

        - PEX-a (Engel-method crosslinked polyethylene), ASTM F876 and F877 (CAN/CSA-B137.5), SDR 9, CTS, 1/2 inch (16 mm) through 3 inch 
(75 mm) nominal pipe size.

**NOTE TO SPECIFIER** Can delete Pre-Sleeved requirement if local code allows PEX directly in slab.

    - Pre-Sleeved Tubing: All PEX tubing that is incased in concrete shall be pre-sleeved in corrugated polyethylene tubing.

      - Pre-sleeved tubing shall be supplied by the PEX tubing manufacturer.

**NOTE TO SPECIFIER** This insulation requirement does not apply to tubing that is required to be insulated per ASHRAE 90.1.

    - Pre-Insulated Tubing: All 1/2 inch (15 mm) to 2 inch (50 mm) PEX tubing that is required to be insulated shall be pre-insulated with minimum 1/2 inch (15 mm) PEX-foam insulation.

      - Pre-insulated tubing shall be supplied by the PEX tubing manufacturer.

    - Manifold Materials: Manifolds shall be manufactured of copper. Manifold connections shall be made to the requirements of ASTM F1960.

      - Manifolds shall be supplied by the PEX tubing manufacturer.

      - PEX-a cold expansion type manifolds shall be an assembly consisting of insert and PEX-a cold expansion ring.

      - Manifold Type: 1 inch Copper Manifold with LF Brass 1/2 inch ProPEX Ball Valve or 1 inch Copper Branch Manifold with 1/2 inch ProPEX LF brass outlets.

    - Multi-Port Tee Materials: Multi-Port Tees shall be manufactured of Engineered Polymers (EP). Multi-Port Tee connections shall be made to the requirements of ASTM F1960.

      - Multi-Port Tees shall be supplied by the PEX tubing manufacturer.

      - PEX-a cold expansion type manifolds shall be an assembly consisting of insert and PEX-a cold expansion ring.

      - Multi-Port Tee Type: Uponor Engineered Polymer (EP) Multi-Port Tee.

    - Fitting Materials: Fittings shall be manufactured of Engineered Polymer (EP). Lead free brass and stainless-steel materials are allowed only for transition fittings. Fitting connections shall be made to the requirements of ASTM F1960.

      - Fittings shall be supplied by the PEX tubing manufacturer.

      - PEX-a cold expansion type fittings shall be an assembly consisting of insert and PEX-a cold expansion ring.

      - Polymer Fitting Type: Uponor Engineered Polymer (EP) fittings.

      - Brass Fitting Type: Uponor lead free brass fittings.

      - Stainless-Steel Fitting Type: Uponor Stainless Steel threaded adapters.

    - Valve Materials: Valves shall be manufactured of lead-free (LF) brass with stainless-steel ball and stem. Valve connections shall be made to the requirements of ASTM F1960.

      - Valves shall be supplied by the PEX tubing manufacturer.

      - PEX-a cold expansion type connections shall be an assembly consisting of insert and PEX-a cold expansion ring.

      - In compliance with 250 CWP, ANSI/NSF 359, ANSI/NSF 372, ANSI/NSF 14/61, ASTM F1960, CAN/CSA B137.5 (ASTM F877).

  - ACCESSORIES

    - Outlet Boxes: Ice Maker and Washing Machine Outlet Boxes shall be supplied by the PEX tubing manufacturer.

    - Fixture Shut-Off Valves: Fixture Shut-Off valves shall be supplied by the PEX tubing manufacturer.

    - Tubing Wall Penetration Brackets: Brackets designed for tubing wall membrane penetrations shall be supplied by PEX tubing manufacturer.

      - Bracket Type: Uponor ProPEX Out-of-the-Wall System.

    - Horizontal Pipe Support Channels: All horizontal pipe supports for PEX sizes 1/2 inch and greater shall be gauge 23 galvanized steel channels and self-gripping and be supplied by the PEX tubing manufacturer.

      - Pipe Support Type: Uponor PEX-a Pipe Support.

  - RELATED MATERIALS

    - Related Materials: Refer to other sections listed in Related Sections paragraph herein for related materials.

- Execution

  - MANUFACTURER’S INSTRUCTIONS

    - Compliance: Comply with manufacturer’s product data, including product technical bulletins, installation instructions, and product carton instructions for installation.

  - EXAMINATION

    - Site Verification of Conditions: Verify conditions which have been previously installed under other sections, are acceptable for PEX tubing system installation in accordance with manufacturer’s instructions.

  - INSTALLATION

    - PEX Potable Water Distribution System:

      - Install PEX tubing in accordance with tubing manufacturer’s recommendations, installation manuals and technical bulletins and as indicated on Contract Drawings including the following;

        - Uponor PEX Piping Systems Design and Installation Manual (PDIM), current edition,

        - Uponor PEX Piping Systems Installation Guide, current edition.

      - White PEX tubing shall not be exposed to direct sunlight for more than thirty (30) days, red and blue PEX tubing shall not be exposed to direct sunlight for more than six (6) months.

      - Insulation must cover the PEX tubing when exposed to a direct UV light source such as fluorescent light bulbs or any UV generating device.

      - Ensure that no glues, solvents, sealants, or chemicals come in contact with the tubing without prior permission from the tube manufacturer.

      - PEX tubing passing through structural concrete slabs shall be pre-sleeved with corrugated polyethylene as supplied by the manufacturer.

      - PEX tubing passing through metal studs shall be use grommets or sleeves at the penetration.

      - Protect PEX tubing with sleeves where abrasion may occur.

      - Use strike protectors where PEX tubing has the potential for being struck with a screw or nail.

      - Manufacturer’s bend supports shall be used where bends are less than 6 times outside pipe diameter.

      - Per code install hangers every 32 inches. For further hanger support use PEX-a pipe support per manufacturer’s recommended installation.

      - The following is a schedule of maximum spacing for hangers and supports for all PEX-a piping using PEX-a pipe support, unless otherwise indicated or required.

| Nominal Pipe Size | System Type | Maximum Support Spacing with PEX-a Pipe Support | Fixed Points |
| --- | --- | --- | --- |
| PEX Pipe 3 Inch and Smaller | Delta T less than or equal to 40°F (22.2°C) (e.g., domestic cold water; chilled water) | 8 feet (2.4 m); clamps not required | Not required |  |
|  | ΔT greater than 40°F (22.2°C) (e.g., domestic hot water; domestic hot-water return; heating hot water) | 8 feet (2.4 m) with clamps every 32 feet (9.7 m) max. | See table on following page |  |

      - The following is a schedule of fixed anchor points.

| Length of Straight Piping Run | Number of Fixed Points* | Fixed Point Spacing |
| --- | --- | --- |
| 0 - 63 ft. (0 - 19.2 m) | 0 | N/A |
| 64 - 128 ft. (19.5 - 39 m) | 1 | Closest support with clamps to center |
| 129 - 192 ft. (39 - 58.5 m) | 2 | Min. 64 ft. (19.5 m) apart |
| 193 - 256 ft. (58.8 - 78 m) | 3 |  |
| 257 - 320 ft. (78.3 - 97.5 m) | 4 |  |

- *Pipes 1 inch and smaller do not require fixed points.

      - All fitting connections to the PEX tubing shall be made to the requirements of ASTM F1960.

      - Ensure the required firestop material defined in the assembly (i.e., sealant) does not come into contact with Uponor EP fittings

      - PEX piping shall be installed per CAN/ULC-S102.2 requirements for plenum applications.

        - Uponor PEX piping manufactured with a maximum nominal OD of 3 inch (80 mm) and encased in 1/2 inch insulation in accordance with Table 3-5 shall have no limitation on spacing (see PEX Piping Systems Design and Installation Manual).

        - Up to and including 2 inch (50 mm) Uponor PEX-a (waterfilled, uninsulated); adjacent runs of waterfilled, uninsulated piping in a return-air plenum have no spacing limitations.

      - Multi-Port Tees shall be used in-suite wherever possible instead of straight or reducing tees to minimize pressure drops in the plumbing distribution system.

      - When system ΔT is greater than 40°F (22°C) midstory guide may be needed to help with expansion and contraction

      - A riser clamp shall be installed on top of every floor and against every second ceiling for all PEX risers.

      - Manufacturer’s wall penetration brackets shall be used at all wall membrane penetrations.

      - Pressurize PEX potable-water distribution system with air or potable water in accordance with applicable codes or per manufacturer’s recommendations.

      - Comply with safety precautions when pressure testing, including use of compressed air, where applicable. Water shall not be used to pressurize the system if ambient air temperature has the possibility of dropping below 32°F 
(0 °C).

    - Related Products Installation: Refer to other sections listed in Related Sections paragraph herein for related products installation.

  - FIELD QUALITY REQUIREMENTS

    - Site Tests (Installation and Post-Installation Testing): [Specify applicable test requirements to be performed during and after product installation].

    - Manufacturer’s Field Services: Provide manufacturer’s field service consisting of product use recommendations and periodic site visits for inspection of product installation in accordance with manufacturer’s instructions.

      - Site Visits: [Specify number and duration of periodic site visits].

  - CLEANING

    - Cleaning: Remove temporary coverings and protection of adjacent work areas. Repair or replace damaged installed products. Clean installed products in accordance with manufacturer’s instructions prior to Owner’s acceptance. Remove construction debris from project site and legally dispose of debris.

    - Water system disinfection

      - Uponor AquaPEX piping should be disinfected in accordance with Uponor Disinfection Guidelines or local codes.

      - Use non-petroleum-based cleaners.

      - Not exceed a pH of 11.

      - Do not allow system to exceed 80 psi.

      - Use a disinfecting solution (chlorine or chloramine) solution of:

        - 200 parts per million (ppm) for 3 hours at a maximum temperature of 77°F (25°C).

        - 50 ppm for 24 hours at a maximum temperature of 77°F (25°C).

        - 4 ppm for 72 hours at a maximum temperature of 140°F (60°C).

      - To prevent reduced service life of system components, disinfection solutions should not stand in the system longer than 72 hours per Uponor Disinfection Guidelines. Flush the system with potable water after disinfection.

      - Chlorine Dioxide is not recommended for system disinfection.

      - Consult piping manufacturer for compatibility if alternative disinfectants are to be used.

  - PROTECTION

    - Protection: Protect installed product and finish surfaces from damage during construction.

### END OF SECTION