## SECTION 15770

### SNOW-MELTING EQUIPMENT

PART 1 GENERAL

  - SUMMARY

- Section Includes: Hydronic snow-melting system.

- Provide labour, materials, transportation, equipment and services to install a hydronic snow-melting system where indicated on the Contract Drawing and specified herein.

- Related Sections:

- Examine all other portions of the subcontract documents for work or other terms and conditions related to the work of this section.

- Provide all work hereunder as required for the support and accommodation of related work.

#### REFERENCES

- General: Standards listed by reference, including revisions by issuing authority, form part of this specification section to extent indicated. Standards listed are identified by issuing authority, authority abbreviation, designation number, title, or other designation established by issuing authority. Standards subsequently referenced herein are referred to by issuing authority abbreviation and standard designation.

- American Society for Testing and Materials (ASTM):

- ASTM F876 Standard Specification for Cross-Linked Polyethylene (PEX) Tubing.

- ASTM F1960 Standard Specification for Cold Expansion Fittings with PEX Reinforcing Rings for Use with Cross-Linked Polyethylene (PEX) Tubing.

- German Institute of Standards (DIN):

1.	DIN 4726 Warm Water Floor Heating Systems and Radiator Connections – Piping Made Out of Plastic Materials.

- Plastic Pipes Institute (PPI):

- PPI Technical Report TR-4/00.

- Uponor, Snow-Melt Design Manual, current edition.

- Uponor, Advanced Design Suite Software.

- Uponor, Installation Handbook, Radiant Floor, current edition.

  - SYSTEM DESCRIPTION

- Performance Requirements: Provide hydronic snow-melting system which has been manufactured, fabricated and installed to comply with regulatory agencies and to maintain performance criteria stated by manufacturer without defects, damage or failure.

  - SUBMITTALS

- General: Submit listed submittals in accordance with Conditions of the Contract and Division 1 Submittal Procedures Section.

- Product Data: Submit product data for specified products.

- Submit verification of Standard Grade hydrostatic pressure ratings from Plastic Pipe Institute in accordance with TR-4/00. The following 3 Standard Grade ratings are required: 200 degrees F (93 Degrees C) at 80 psi (551 kPa); 180 degrees F (82 degrees C) at 100 psi (689 kPa) and 73.4 degrees F (23 degrees C) at 160 psi (1102 kPa).

- Submit Product Submittal sheets for tubing, manifolds, connection system, zone controls, water temperature controls and snow-melting control.

- Regulatory Listings: Where the PEX Snow Melt System is subject to the requirements of local or provincial building codes, submit appropriate ULC or Warnock Hersey listings as proof of compliance with provincial building codes.

- Submit listings that indicate that the PEX tubing system has been listed to CAN/ULC-S101 when the PEX tubing is incorporated in and traverses a CAN/ULC-S101 floor/ceiling assembly. The listings must be appropriate to assemblies on site.

- Submit listings that indicate that the PEX tubing firestop system has been listed to CAN/ULC-S115 when the PEX tubing penetrates a fire separation. The listings must be appropriate to assemblies on site.

- Submit listings that indicate that the PEX tubing has been listed to CAN/ULC-S102.2 for maximum 25 flame spread and maximum 50 smoke developed.

- Submit approval from the Authority Having Jurisdiction (AHJ) that the PEX Radiant Floor Heating System meets the building code requirements in the jurisdiction that the system is to be installed.

- Shop Drawings: Submit design print-out of Uponor Advanced Design Suite,  control schematic and shop drawings indicating loop layout, manifold locations, loop flow balance settings, slab profiles, and product components, including anchorage, accessories and finishes.

- Include installation drawings of tubing layout indicating loop length, loop spacing, tube size and detail notes to aid in installation of system.

- Include control schematic indicating heat source, mechanical piping and accessories from heat source to manifolds, circulators, water tempering and zone controls. Also indicate supply water temperatures and flow rates to manifolds.

- No fabrication shall be performed until approval is given.

- Quality Assurance Submittals: Submit the following:

- Copy of certificate indicating that the installer is certified in the installation of the manufacturer’s products.

- Manufacturer’s Instructions: Manufacturer’s installation instructions.

- Installer shall provide in writing to the project owner that the PEX tubing and components furnished under this specification conforms to the material and mechanical requirements specified herein.

- Closeout Submittals: Submit the following:

- Operation and Maintenance Data: Operation and maintenance data for installed products in accordance with Division 1 Closeout Submittals (Maintenance Data and Operation Data) Section including methods for maintaining installed products and precautions against cleaning materials and methods detrimental to finishes and performance.

- Warranty: Warranty documents specified herein.

- Manufacturer’s Field Reports: Manufacturer’s field reports specified herein.

- Final “As-Built” loop layout drawing.

- Control schematic.

- Copy of Uponor Advanced Design Suite software printout.

- Record Documents: Project record documents for installed materials in accordance with Division 1 Closeout Submittals (Project Record Documents) Section.

  - QUALITY ASSURANCE

- Qualifications:

- Installer Qualifications: Installer shall be experienced in performing work of this section who has specialized in installation of work similar to that required for this project.

- Installation Qualifications: Installation must be by skilled tradesmen holding a trade qualification license or apprentices under the supervision of a licensed tradesman.

- Regulatory Requirements: PEX tubing and components shall be installed in full compliance with all provincial and local jurisdictional codes, standards and requirements. In particular:

- PEX tubing shall be listed to a maximum 25 flame spread and maximum of 50 smoke developed per the requirements of CAN/ULC-S102.2.

- PEX tubing penetrating a fire separation shall be sealed per CAN/ULC-S115.

- PEX tubing contained within a CAN/ULC-S101 floor/ceiling assembly shall be listed per CAN/ULC-S101.

- Pre-installation Meetings: Conduct pre-installation meeting to verify project requirements, substrate conditions, manufacturer’s installation instructions and manufacturer’s warranty requirements. Comply with Division 1 Project Management and Coordination (Project Meetings) Section.

  - DELIVERY, STORAGE AND HANDLING

- General: Comply with Division 1 Product Requirements Sections.

- Ordering: Comply with manufacturer’s ordering instructions and lead-time requirements to avoid construction delays.

- Delivery: Deliver materials to job site in manufacturer’s original, unopened, undamaged containers with identification labels intact.

- Storage and Protection: Store materials protected from exposure to harmful weather and job site conditions.

- Store PEX tubing in cartons or under cover to avoid dirt or foreign material from being introduced into the tubing.

- Do not expose PEX tubing to direct sunlight for more than 30 days. If construction delays are encountered, installer is responsible for providing cover to portions of tubing exposed to direct sunlight.

  - WARRANTY

- Project Warranty: Refer to Conditions of the Contract for project warranty provisions.

- PEX Manufacturer’s Warranty:

- PEX tubing shall carry a 25-year non-prorated warranty against failure due to defect in material or workmanship.

- Manifolds and fittings shall carry a 5-year non-prorated warranty against failure due to defect in material or workmanship.

- Controls and electrical components shall carry a 2-year non-prorated warranty against failure due to defect in material or workmanship.

- Warranty shall provide for repair or replacement of any tube or fittings which are proven to be defective and pay for consequential damages.

- Warranty shall be transferable to subsequent owners.

- Effective Warranty: Current manufacturer’s warranty at time of installation.

- Warranty Period: Warranty shall commence on Date of Substantial Completion.

  - SYSTEM STARTUP AND OWNER’S INSTRUCTION

- System Startup: [Specify system startup requirements].

- Owner’s Instruction: Instruct Owner’s personnel in operation and maintenance of installed units. Provide manufacturer’s installation, operation and maintenance instructions for installed units.

PART 2 PRODUCTS

2.01	SNOW-MELTING SYSTEM

- Manufacturer: Uponor Ltd.

- Proprietary System: Uponor hePEX plus Snow-Melting System.

2.02	PRODUCT SUBSTITUTIONS

- Substitutions: No substitutions permitted.

2.03	MATERIALS

- Tube Materials: Tube shall be cross-linked polyethylene (PEX) manufactured by PEX-A or peroxide method.

- Tubing Type: Uponor hePEX plus tubing.

- Oxygen Barrier: Tube shall have an oxygen barrier capable of limiting oxygen migration through the tube wall to no greater than 0.10 g/m3/day at 104 degree F (40 degrees C) water temperature per the requirements of DIN 4726.

- PEX tubing shall be manufactured in accordance with ASTM F876. The tube shall be listed to ASTM by an independent third party agency.

- PEX tubing shall have Standard Grade hydrostatic design and pressure ratings of 200 F (82 degrees C) at 80 psi (551 kPa), 180 degrees F (82 degrees C) at 100 psi (689 kPA), and 73.4 degrees F (23 degrees C) at 160 psi (1102 kPa). Temperature and pressure ratings shall be issued by the Plastic Pipe Institute (PPI), a division of the Society of the Plastic Industry (SPI).

- Minimum bend radius for cold bending of the PEX tubing shall not be less than 6 times the outside diameter. Bends with a radius less than stated shall require the use of a bend support as supplied by tube manufacturer.

- PEX tubing dimensions shall be:

- 5/8” nominal inside diameter in accordance with ASTM F876 or,

- ¾” nominal inside diameter in accordance with ASTM F876 or,

- 1” nominal inside diameter in accordance with ASTM F876 as indicated on contract drawings.

[Note to specifier: Select one of the “B.” listed below for desired type of manifolds. Brass 1-1/2” Tru-flow Classic, 1-1/4” Tru-flow Junior, 1-1/4” Engineered Plastic (EP)]

- Manifold Materials: Manifold shall be fully assembled and mounted on a durable bracket with an end cap on the supply manifold and an endcap with vent and drain on the return manifold. Manifold shall have 1-1/2” internal I.D. for full-flow characteristics. Manifold shall have R32 unions on the inlet side of the manifold to allow for various connection adapters. Inlet side temperature gauges with strainer and shutoff valve will provide full manifold isolation. Each loop outlet shall have a visual flow indicator for balancing purposes.

- Manifold Type: Uponor Tru-flow Classic Manifold.

2.	Manifolds shall be supplied by the PEX tubing manufacturer.

- Manifolds shall have integral manual air vents on return

- Manifolds shall be manufactured from Brass.

- Manifolds shall be supplied with manufacturers mounting brackets.

- Manifolds shall be supplied with visual flow indicators.

- Manifold Materials: Manifold shall be fully assembled and mounted on a durable bracket with an end cap on the supply manifold and an endcap with vent and drain on the return manifold. Manifold shall have 1-1/4” internal I.D. for full-flow characteristics. Manifold shall have R32 unions on the inlet side of the manifold to allow for various connection adapters. Inlet side temperature gauges with strainer and shutoff valve will provide full manifold isolation. Each loop outlet shall have a visual flow indicator for balancing purposes.

- Manifold Type: Uponor Tru-flow Junior Manifold.

2.	Manifolds shall be supplied by the PEX tubing manufacturer.

- Manifolds shall have integral manual air vents on return

- Manifolds shall be manufactured from Brass.

- Manifolds shall be supplied with manufacturers mounting brackets.

- Manifolds shall be supplied with visual flow indicators.

- Manifold Materials: Engineered Plastic (EP) manifold shall be fully assembled and mounted on a durable bracket with air vents and drains on both the supply and return manifold sections. Manifold shall have 1-1/4” internal I.D. for full-flow characteristics. Manifold shall have R32 unions on the inlet side of the manifold to allow for various connection adapters. Visual flow meters shall be pre-mounted on the manifold assembly. Manifold shall be capable of full flow isolation on each loop.

- Manifold Type: Uponor Engineered Plastic (EP) Manifold.

2.	Manifolds shall be supplied by the PEX tubing manufacturer.

- Manifolds shall have integral manual air vents on supply and return

- Manifolds shall be manufactured from Engineered Plastic (EP).

- Manifolds shall be supplied with manufacturers mounting brackets.

- Manifolds shall be pre-assembled with visual flow indicators.

- Fitting Materials: Fittings shall be manufactured of polysulfone or dezincification resistant brass. Fittings shall be nose cone insert type compression fitting, nose cone insert type swivel fitting or PEX-A cold expansion type fitting.

- Fittings shall be supplied by the PEX tubing manufacturer.

- Compression fitting shall be an assembly consisting of nose cone insert, compression ring and compression nut.

- Swivel fitting shall be an assembly consisting of nose cone insert, swivel nut and PEX-A cold expansion ring.

- PEX-A cold expansion type fitting shall be an assembly consisting of insert and PEX-A cold expansion ring.

- Supply and Return Piping to Manifolds: Piping run in heated spaces shall be cross-linked tube with oxygen diffusion barrier capable of limiting oxygen migration through the tube wall to no greater than 0.10 g/m3/day at 104 degree F (40 degrees C) water temperature per the requirements of DIN 4726. Supply and return piping run underground shall be cross-linked tube encased in a pre-insulated polyethylene corrugated jacket.

- Supply and Return Piping Type: Uponor HePEX tubing

- Pre-insulated Supply and Return Piping Type: Uponor Ecoflex

- Frost Protection: The heat transfer fluid shall be solution of 50% glycol and 50% water.

1. 	Glycol Type: Propylene Glycol

2.04	ACCESSORIES

- Snow-Melting Control: Snow-Melting control shall be supplied by the PEX tubing manufacturer and be able to perform the following functions,

- Automatically turn on the snow-melting system when snow or ice is forming on the slab.

- Automatically turn off the snow-melting system when snow or ice has been melted.

- Idle the slab to minimize slab temperature ramp up times. [Specify if required].

- Control the heating up of the slab from cold starts to minimize thermal shock.

- Protect heating source from freezing.

- Enable heat source.

- Control system and secondary pumps.

- All wiring to mechanical equipment shall be with Cat5 wiring.

- Snow-Melting Control Type: Uponor Comfort Control Multifunction

  - RELATED MATERIALS

- Related Materials: Refer to other sections listed in Related Sections paragraph herein for related materials.

PART 3 EXECUTION

3.01	MANUFACTURER’S INSTRUCTIONS

- Compliance: Comply with manufacturer’s product data, including product technical bulletins, installation instructions and product carton instructions for installation.

3.02	EXAMINATION

- Site Verification of Conditions: Verify substrate conditions which have been previously installed under other sections, are acceptable for installation in accordance with manufacturer’s instructions.

3.04	INSTALLATION

- Snow-Melting Installation:

- Install hydronic snow-melting tubing loops in accordance with tubing manufacturer’s recommendations and as indicated on Contract Drawings. Installation shall follow shop drawings for tube layout, tube spacing, manifold configuration, manifold location, and controls. Comply with notes on shop drawings.

- Manifolds supply and return piping shall be isolated with ball valves.

- Fittings and manifolds shall be accessible for maintenance. The only exceptions are for repair splice with manufacturer’s approved fittings and procedure for concealed connections.

- Install tubing loops without splices. It is acceptable to install a repair splice within the embedded loop should on-site damage occur and an emergency repair be authorized. Refer to PEX tubing manufacturer’s installation handbook for instructions on the proper installation of the repair splice.

- Ensure that no glues, solvents, sealants or chemicals come in contact with the tubing without prior permission from the tube manufacturer.

- Manufacturer’s bend supports shall be used where tubing enters and exits the slab.

- Methods of tubing attachment shall be to manufacturer’s installation handbook.

- Pressurize tubing system with air or water in accordance with applicable codes or, in the absence of applicable codes, to a pressure of 60-psi (413 kPa) for 24 hours prior to encasement of tubing system. Tubing shall remain pressurized during encasement and for a period of 24 hours thereafter to ensure system integrity.

- Comply with safety precautions when pressure testing, including use of compressed air, where applicable. Water shall not be used to pressurize the system if ambient air temperature has the possibility of dropping below 32 degrees F (0 degrees C).

- Ensure system is freeze proof should ambient air temperature be anticipated to drop below 32 degrees F (0 degrees C) and the system is not under full operation.

- Balancing: Adjust flow to all loops as indicated on shop drawings.

- System shall not be operated during panel concrete curing period unless permission has been granted and specific instructions on panel pre-heating has been provided.

- Related Products Installation: Refer to other sections listed in Related Sections paragraph herein for related products installation.

3.05	FIELD QUALITY REQUIREMENTS

- Site Tests (Installation and Post-Installation Testing): [Specify applicable test requirements to be preformed during and after product installation].

- Manufacturer’s Field Services: Provide manufacturer’s field service consisting of product use recommendations and periodic site visit for inspection of product installation in accordance with manufacturer’s instructions.

- Site Visits: [Specify number and duration of periodic site visits.].

3.07	CLEANING

- Cleaning: Remove temporary coverings and protection of adjacent work areas. Repair or replace damaged installed products. Clean installed products in accordance with manufacturer’s instructions prior to Owner’s acceptance. Remove construction debris from project site and legally dispose of debris.

3.08	PROTECTION

- Protection: Protect installed product and finish surfaces from damage during construction.

### END OF SECTION